## Sheet1
T3-6CTA
Address
| Bytes | Register & Description
0 to 3 | 4 | Serial Number 4 Bytes value
4 | 1 | EPROM hardware Version Number
5 | 1 | Firmware Version Number
6 | 1 | Modbus device address
7 | 1 | Product Model
8 | 1 | Hardware Revision
9 | 1 | PIC Version Number
10 to 12 | Reserved | Reserved
13 | 1 | Calibration Register-Used to calibrate the outputs
14 | Reserved | Reserved
15 | 1 | Baudrate Setting: 0 = 9600bps, 1 = 19200bps
19 | 1 | MODBUS RESPONSE DELAY DEFAULT 0 = 2.5MS 1 = 7.5MS
20 to 99 | Reserved | Reserved
100 | 2 | Output 1 Register
101 | 2 | Output 2 Register
102 | 2 | Output 1 Switch Bank
103 | 2 | Output 2 Switch Bank
104 | 2 | Analog Input 1 High Byte
105 | 2 | Analog Input 1 Low Byte
106 | 2 | Analog Input 2 High Byte
107 | 2 | Analog Input 2 Low Byte
108 | 2 | Analog Input 3 High Byte
109 | 2 | Analog Input 3 Low Byte
110 | 2 | Analog Input 4 High Byte
111 | 2 | Analog Input 4 Low Byte
112 | 2 | Analog Input 5 High Byte
113 | 2 | Analog Input 5 Low Byte
114 | 2 | Analog Input 6 High Byte
115 | 2 | Analog Input 6 Low Byte
116 | 2 | Analog Input 7 High Byte
117 | 2 | Analog Input 7 Low Byte
118 | 2 | Analog Input 8 High Byte
119 | 2 | Analog Input 8 Low Byte
120 | 2 | Analog Input 9 High Byte / AirFlow High Byte for Type2
121 | 2 | Analog Input 9 Low Byte / AirFlow Low Byte for Type2
122 | 2 | Analog Input 10 High Byte
123 | 2 | Analog Input 10 Low Byte
124 | 2 | Analog Input 11 High Byte / CT Input 1 High Byte for Type 2
125 | 2 | Analog Input 11 Low Byte / CT Input 1 Low Byte for Type 2
126 | 2 | Analog Input 12 High Byte / CT Input 2 High Byte for Type 2
127 | 2 | Analog Input 12 Low Byte / CT Input 2 Low Byte for Type 2
128 | 2 | Analog Input 13 High Byte / CT Input 3 High Byte for Type 2
129 | 2 | Analog Input 13 Low Byte / CT Input 3 Low Byte for Type 2
130 | 2 | CT Input 1 High Byte / CT Input 4 High Byte for Type 2
131 | 2 | CT Input 1 Low Byte / CT Input 4 Low Byte for Type 2
132 | 2 | CT Input 2 High Byte / CT Input 5 High Byte for Type 2
133 | 2 | CT Input 2 Low Byte / CT Input 5 Low Byte for Type 2
134 | 2 | CT Input 3 High Byte / CT Input 6 High Byte for Type 2
135 | 2 | CT Input 3 Low Byte / CT Input 6 Low Byte for Type 2
136 | 2 | CT Input 4 High Byte
137 | 2 | CT Input 4 Low Byte / Outdoor light sensor temperature
138 | 2 | CT Input 5 High Byte
139 | 2 | CT Input 5 Low Byte / Outdoor light sensor humidity
140 | 2 | CT Input 6 High Byte
141 | 2 | CT Input 6 Low Byte / Outdoor light sensor luminance
501-579 are only for test revision
501 | 1 | RFM69 RegOpMode
502 | 1 | RFM69 RegDataModul
503 | 1 | RFM69 RegBitrateMsb
504 | 1 | RFM69 RegBitrateLsb
505 | 1 | RFM69 RegFdevMsb
506 | 1 | RFM69 RegFdevLsb
507 | 1 | RFM69 RegFrfMsb
508 | 1 | RFM69 RegFrfMid
509 | 1 | RFM69 RegFrflSB
510 | 1 | RFM69 RegOsc1
511 | 1 | RFM69 RegAfcCtrl
512 | 1 | RFM69 Reserved0C
513 | 1 | RFM69 RegListen1
514 | 1 | RFM69 RegListen2
515 | 1 | RFM69 RegListen3
516 | 1 | RFM69 RegVersion
517 | 1 | RFM69 RegPaLevel
518 | 1 | RFM69 RegPaRamp
519 | 1 | RFM69 RegOcp
524 | 1 | RFM69 RegLna
525 | 1 | RFM69 RegRxBw
526 | 1 | RFM69 RegAfcBw
527 | 1 | RFM69 RegOokPeak
528 | 1 | RFM69 RegOokAvg
529 | 1 | RFM69 RegOokFix
530 | 1 | RFM69 RegAfcFei
531 | 1 | RFM69 RegAfcMsb
532 | 1 | RFM69 RegAfcLsb
533 | 1 | RFM69 RegFeiMsb
534 | 1 | RFM69 RegFeiLsb
535 | 1 | RFM69 RegRssiConfig
536 | 1 | RFM69 RegRssiValue
537 | 1 | RFM69 RegDioMapping1
538 | 1 | RFM69 RegDioMapping2
539 | 1 | RFM69 RegIrqFlags1
540 | 1 | RFM69 RegIrqFlags2
541 | 1 | RFM69 RegRssiThresh
542 | 1 | RFM69 RegRxTimeout1
543 | 1 | RFM69 RegRxTimeout2
544 | 1 | RFM69 RegPreambleMsb
545 | 1 | RFM69 RegPreambleLsb
546 | 1 | RFM69 RegSyncConfig
547 | 1 | RFM69 RegSyncValue1
548 | 1 | RFM69 RegSyncValue2
549 | 1 | RFM69 RegSyncValue3
550 | 1 | RFM69 RegSyncValue4
551 | 1 | RFM69 RegSyncValue5
552 | 1 | RFM69 RegSyncValue6
553 | 1 | RFM69 RegSyncValue7
554 | 1 | RFM69 RegSyncValue8
555 | 1 | RFM69 RegPacketConfig1
556 | 1 | RFM69 RegPayloadLength
557 | 1 | RFM69 RegNodeAdrs
558 | 1 | RFM69 RegBroadcastAdrs
559 | 1 | RFM69 RegAutoModes
560 | 1 | RFM69 RegFifoThresh
561 | 1 | RFM69 RegPacketConfig2
562-577 | 1 | RFM69 RegAesKey1 - RFM69 RegAesKey16
578 | 1 | RFM69 RegTemp1
579 | 1 | RFM69 RegTemp2
599 | 1 | RFM69 Module Exist
600 | 2 | RFM69 Module Encrypt Key 1
601 | 2 | RFM69 Module Encrypt Key 2
602 | 2 | RFM69 Module Encrypt Key 3
603 | 2 | RFM69 Module Encrypt Key 4
604 | 2 | RFM69 Module Encrypt Key 5
605 | 2 | RFM69 Module Encrypt Key 6
606 | 2 | RFM69 Module Encrypt Key 7
607 | 2 | RFM69 Module Encrypt Key 8
608 | 2 | RFM69 Module Network ID
609 | 2 | RFM69 Module Node ID
610 | 2 | RFM69 Module Frequnce High Byte
611 | 2 | RFM69 Module Frequnce Low Byte
612 | 2 | RFM69 Module Encryption Enable
613 | 1 | RFM69 Module Deadmaster Value ( 10 means 1 second)
614 | 2 | RFM69 Module bitrate
615 | 1 | RFM69 Module signal strength(RSSI)
616 | 1 | RFM69 Module Deadmaster Switch (1-enable, 0-disable. default is disable)
679 | 2 | Accelero X-axis value
680 | 2 | Accelero Y-axis value
681 | 2 | Accelero Z-axis value
682 | 2 | Accelero Sensitivity Low Line
683 | 2 | Accelero Sensitivity High Line (1023 is biggest)
684 | 1 | Switch to control RS485 to a master or slave, for reading outdoor light sensor( 1 is master, 0 is slave)
685 | 1 | RS485 slave device modbus ID
686 | 2 | Gyroscope X-axis value
687 | 2 | Gyroscope Y-axis value
688 | 2 | Gyroscope Z-axis value
689 ~ 698 | 1 | Accelero and Gyroscope chip's configuration registers (CTRL1_XL(10H)-CTRL10_C(19H)) (only for type 3)
699 | 1 | Set 1 to reset Acc & Gyro chip's registers to default, and reboot the board
1002 | 2 | Air Flow Pressure filter(1-10)
1003 | 2 | ad value
1004 | 2 | prssure(0.01inWC)
1005 | 1 | Air Flow Pressure Table Select(0 = factory table, 1 = user table)
1008 | 2 | Air Flow Pressure Calculate Point number
1009 ~ 1028 |  | the factory calibrate point.
1029 | 2 | Air Flow Pressure User Calculate Point number
1030~1049 | 2 | the user calibrate table point.
1052 |  | flow Rate (0.1 m/s or 0.1 fps)
1053 |  | Air Flow value,float type High Byte( m³/s or cfm)
1054 |  | Air Flow Value ,float type Low Byte( m³/s or cfm)
1055 |  | Air Flow Unit(0 = metric, 1 =Imperial units)
1056 |  | Duct Area( 0.001㎡ or 0.001ft²）
10000-10022 |  | output 1 block
10023-10045 |  | output 2 block
11472-11494 |  | input 1 block
11495-11517 |  | input 2 block
… |  | …
20001 | 2 | CT Input 1 Current Low Byte
20002 | 2 | CT Input 2 Current Low Byte
20003 | 2 | CT Input 3 Current Low Byte
20004 | 2 | CT Input 4 Current Low Byte
20005 | 2 | CT Input 5 Current Low Byte
20006 | 2 | CT Input 6 Current Low Byte
20007 | 2 | Analog Input 1 Low Byte
20008 | 2 | Analog Input 2 Low Byte
20009 | 2 | Analog Input 3 Low Byte
20010 | 2 | Analog Input 4 Low Byte
20011 | 2 | Analog Input 5 Low Byte
20012 | 2 | Analog Input 6 Low Byte
20013 | 2 | Analog Input 7 Low Byte
20014 | 2 | Analog Input 8 Low Byte
20015 | 2 | Analog Input 9 Low Byte / Accelerometer Low Byte for Type2
20016 | 2 | Analog Input 10 Low Byte / Airflow Low Byte for Type2
20017 | 2 | Analog Input 11 Low Byte / Outdoor Temp Low Byte for Type 2
20018 | 2 | Analog Input 12 Low Byte / Outdoor Hum Low Byte for Type 2
20019 | 2 | Analog Input 13 Low Byte / Outdoor Lux Low Byte for Type 2
20020 | 2 | Output 1 Register
20021 | 2 | Output 2 Register